## 1 Preliminaries
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow all preliminaries in connection with the works. This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
| 1 | PRELIMINARIES AND GENERAL
This schedule of works is to be read in conjunction with the specification . It will be expected that the contractor has allowed for all elements indicated on the specification and schedule, as well as having inspected the site prior to returning the tender.
All works are to be undertaken by suitably qualified specialists where applicable with relevant experience in working upon historic buildings.
The main contractor will be responsible for coordinating all relevant domestic and named sub-contractors, and the like, and the associated materials and labour. The Contract Administrator is to be furnished with a suitable programme of work to adequately describe the critical path programming. The contractor will be expected to keep adequate supervisory personnel on site at all times in the form of a site agent/foreman.
Buildings: Site Meetings with the Client and Architect can take place within the Museum.
Power: A power supply located in the Museum will be made available for the Contractor’s use. The Contractor will be responsible for connecting to the supply.
Lavatories: The WCs within the Museum will be available for the Contractor’s use, as long as they are kept in good order.
Parking: The adjacent car park provides ample parking. This is a pay-and-display car park owned by Shropshire County Council. This is a public car park and is well used.
Deliveries: Deliveries to be via the car park and to the scaffold enclosures.
Contractors to note that the work descriptions below are for tender purposes and not necessarily in order of works on site.
Photographs: Prior to commencement of the contract, the main Contractor is to take a full set of condition photographs, internally and externally, and issue a set of colour copies, annotated to indicate the date taken and location, to the Architect. It is acceptable to submit a CD of digital photographs with an appropriately referenced list.
Protection:
During the course of the contract, temporary protection is to be provided as follows:-
· Dust control measures to prevent dust and rain from entering the Museum. In addition, provide polythene sheeting to be laid over the adjacent internal features.
· Dust sheeting below the working areas and to all walkways.
Bats: There is no known bat activity on the site. The contractor is to remain vigilant and advise the Architect immediately on discovery of a bat.
Asbestos: Asbestos is noted in the DB's However,The contractor is to remain vigilant and advise of any potential ACM
On Completion: The Contractor is to undertake an external and internal clean of the site to remove all dust and debris consequent upon the works.
| 1.01 | Outline Works
| 1.01.1 | Electrical work required to support Local Exhaust Ventilation (LEV) installation at Blists Hill Victorian Town, Madeley, Telford.Paint shop, Fettling shop and Foundry
| 1.01.2 | Paint shop:
Electrical supply required – 3 Phase, 400V, 50Hz, 10amp with D Type Breaker. Complete electrical install (LEV contractor will supply starter).Electrical wiring for ductwork package and fan installation
| 1.01.3 | Fettling shop:
Grinding Filter -Electrical supply required – 3 Phase, 400V, 50Hz, 10amp with D Type Breaker .Complete electrical install (LEV contractor will supply starter). Down Draft Bench - Electrical supply required – 1 Phase, 230V, 50Hz, 13amp (3 pin socket).Electrical control wiring (as necessary)
| 1.01.64 | Foundry:
Chalk mould and press,Electrical supply required – 3 Phase, 400V, 50Hz, 10amp with D Type Breaker .Complete electrical install (LEV contractor will supply starter).Electrical control wiring (as necessary)
| 1.02 | Preliminaries
Refer to IGMT Preliminires and Specification , Allow for costs associated with works described there, eg site set up, H&S, protection, access and day works.
Provide a breakdown of these costs on a marked up version of the above.
| 1.02.1 | Prelims, OH&P, site set up costs etc. | 1 | Item
| 1.03 | Access
| 1.03.1 | Erect and maintain an independent access tower with lifts to allow full accessin order to carry out the works as described. , protecting the public and any footpath closures required in carrying out the works. Ensure that all precautions are taken to reduce the risk of unauthorised access, removing towers at the end of every day or locking them away. | 1 | Item
0
[5 empty] | Item 1 Total | 0
To be carried forward to Collection

## 2 Enabling Electrical Works
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow all preliminaries in connection with the works. This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
General notes
| 2 | ENABLING SUPPLIES FOR FETTLING /PAINT SHOP
| 2.01 | Supply & install new sub-main from north feeder pillar to warehouse DB. include for civil works as required though the main street etc.
| 2.02 | Supply & installation of new panel board within warehouse to replace existing (DBSMP/WS)
| 2.03 | Supply & installation of new TPN DB within warehouse to replace existing (DBWS)
| 2.04 | Supply & installation of new TPN DB for fettling shop (DB/CF1)
[5 empty] | Item 2 Total | 0
|  |  |  | To be carried forward to Collection |  | 0

## 3 Remedial Works
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow all preliminaries in connection with the works. This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
General notes
| 3 | REMEDIAL ELECTRICAL WORKS
| 3.01 | Carry out the following remedial works as noted in EIC Report 27279499 Continuation sheet for part 6 observations and recommendations for actions to be taken.
| 3.02 | Item 37 DB FOUNDRY- 5TP NO ACCESS TO TEST (LIM) Provide cost for investigation
| 3.03 | Item 38 DBSMP/WS 1TP LIMITATION TO VERIFY (LIM) Provide cost for investigation
| 3.04 | Item 39 DBSMP/WS- ALL ZS READINGS EXCEED MAX PERMITTED DUE TO INCOMING READING (C2)
| 3.05 | Item 40 DBSMP/WS-ALL CIRCUITS OFF SUBBOARDS HAVE HIGH ZS DUE TO INCOMER (C2)
| 3.06 | Item 41 DBSMP/WS 2TP- SUPPLY CABLE SHOWING SIGNS OFF DEGRADATION (F1) Provide Cost to replace
| 3.07 | Item 54 DB ENGINEERS ALL- NO FLYLEADS FITTED FOR SWA SHEATH CPC (C2)
| 3.08 | Item 55 DB DB ENGINEERS 8L3- SOCKET NOT FIXED TO WALL (C2)
| 3.09 | Item 56 DB ENGINEERS 2L2- FLOOD LIGHT TO HIGH NO ACCESS (LIM) Provide cost for investigation
| 3.1 | Item 57 DB ENGINEERS 7L3- NO ACCESS TO OFFICE (LIM)Provide cost for investigation
| 3.11 | Item 58 DB ENGINNERS DB-BLANKS MISSING IN DB. ACCESS TO LIVE PARTS (C1)
| 3.12 | Item 59 DB ENGINEERS 3TP- 20MM HOLE IN BOTTOM OF ISOLATOR (C2)
| 3.13 | Item 60 DB MP ENGINEERS DB-MULTIPLE HOLES IN DB, ACCESS TO LIVE PARTS (C1)
| 3.14 | Item 61 DBMP ENGINEERS DB- MULTIPLE FUSE CARRIERS MISSING DIRECT ACCESS TO LIVE PARTS (C1)
| 3.15 | Item 62 DB MP ENGINNERS- 3L1/8TP- CIRCUIT NOT FOUND UNABLE TO VERIFY ELECTRICAL SAFETY (F1)Provide cost for investigation
| 3.16 | Item 63 DB MP ENGINNERS, 1L1- CABLE SIZE TO SMALL FOR OVERCURRENT PROTECTION (C2)
| 3.17 | Item 64 DB MP ENGINEERS DB- NO FLYLEADS ON ANY SWITCHES FOR CPC CONTINUITY (C2)
| 3.18 | Item 65 DB MP ENGINEERS- 4TP- UNABLE TO TEST DUE TO ASBESTOS IN DB (LIM)Provide cost for investigation
| 3.19 | Item 66 DB WAREHOUSE BEHIND- UNABLE TO TEST DUE TO ASBESTOS IN DB (LIM)Provide cost for investigation
| 3.2 | Item67 DBSMP/WS- ALL ZS READINGS OFF SUB BOARDS ARE HIGH DUE TO EARTH ISSUE ON THIS DB CAUSING MAX ZS ISSUES (C2)
| 3.21 | Item 72 DBCS1-9L2, 10L1-NO RCD ON SOCKETS (C2)
| 3.22 | Item 73 DBCS1 DB- 32MM HOLE IN BOTTOM OF DB (C1)
| 3.23 | Item 74 DBCS1-4TP-SOCKET HANGING OFF WALL (C2)
| 3.24 | Item 75 DBCS1- 9L2- BROKEN 2G SOCKET ON SWITCH CRACKED (C2)
| 3.25 | Item 76 DBCS1-7TP, 9L1- CABLES NOT FIXED TO FABRIC OF BUILDING (C2)
| 3.26 | Item 77 DBCS1 8L2- 2 X RADIALS DOUBLED UP ON 32A RCBO. CPD OVERRATED FOR CABLE CURRENT CARRYING CAPACITY (C2)
| 3.27 | Item 84 DBWS-3L2/3L1/2L3-CIRCUIT NOT FOUND UNABLE TO VERIFY ELECTRICAL SAFETY (F1)Provide cost for investigation
| 3.28 | Item 85 DBWS-DB- VARIOUS CABLES LEFT CUT OFF IN DB NOT BONDED TO EARTH (C3)
| 3.29 | Item 86 DBWS DB- VARIOUS SWAS HAVE NO FLYLEAD FOR SWA EARTH CONTINUITY (C3)
| 3.3 | Item 87 DBWS-11L2/12L1- NO RCDS ON SOCKETS (C2)
| 3.31 | Item 88 DBWS-9TP-ASBESTOS FLASH ARRESTORS IN DB (LIM)Provide cost for investigation
| 3.32 | Item 91 DBWS-2L3, 3L1, 3L2- CIRCUIT NOT FOUND UNABLE TO VERIFY ELECTRICAL SAFETY (F1)Provide cost for investigation
| 3.33 | Item 111 DBSMP WS DB- HIGH ZS READING AT DB (F1)Provide cost for investigation
| 3.34 | Item 181 DB FOUNDRY-3L2- 4 X JOINTS ON LIGHTS TAPED UP (C2)
| 3.35 | Item 182 DB FOUNDRY-3L2- 4 X JOINTS ON LIGHTS TAPED UP (C3)
| 3.36 | Item 183 DB FOUNDRY 1L2,8L3, 3L1- NO RCD ON SOCKETS (C2)
| 3.37 | Item 184 DB FOUNDRY 11TP- NO RCD ON SOCKETS (C2)
| 3.38 | Item 185 DB FOUNDRY- 1L1- CIRCUIT NOT FOUND UNABLE TO VERIFY ELECTRICAL SAFETY (F1) Provide Cost for Investigation
| 3.39 | Item 204 DB FOUNDRY DB- NO MAIN EARTH OFF INCOMING GLAND FITTED CAUSING HIGH ZS THROUGHOUT (C2)
| 3.4 | Item 205 DB FOUNDRY 6TP- 20MM HOLE IN BOTTOM OF ISOLATOR- SIGNS OF CORROSION (C2)
| 3.41 | Item 206 DB FOUNDRY 2TP- NO FLYLEAD OR BANJO- NO EARTH ON CIRCUIT (C1)
| 3.42 | Item 207 DB FOUNDRY 9TP- SWA GLANDED INTO CONDUIT- REGLAND AND ADD FLYLEAD (C1)
| 3.43 | Item 208 DB FOUNDRY 11TP- NO FLYHEAD OR BANJO- NO EARTH ON CIRCUIT (C1)
| 3.44 | Item 209 DB FOUNDRY 14L3- NO FLYHEAD FITTED (C2)
| 3.45 | Item 210 DB FOUNDRY- 14L3 4 CORE SWA USED AS RING MAIN WITH ARMOURING USED AS CPC (C3)
| 3.46 | Item 266 DB FOUNDRY - maximum Zs exceeded on all circuits due to incoming earthing issues (C1)
[5 empty] | Item 3 Total | 0
|  |  |  | To be carried forward to Collection |  | 0

## 4 Fettling-Paint Shop Works
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow all preliminaries in connection with the works. This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
General notes
| 4 | FETTLING & PAINT SHOPS NEW WORKS TO FACILITATE LEV UPGRADES
| 4.01 | Rewire all machines within fettling shop.
| 4.02 | Install new lighting within Paint & Fettling shop including emergency lighting .
| 4.03 | Rewire all socket outlets, extract etc within painting shop.
| 4.04 | Installation new sub-mains to the following new distribution boards: DB Warehouse, DBWS & DB/CS1 Include for high level access as required.
| 4.05 | Replace Sub-main & DB to fettling, paint shops & wash rooms. Note: for works to be carried out within these areas the Zs needs to be improved, Note: the current switchgear & paper wrapped sub-mains are not up to current regulations etc .
| 4.06 | All existing outgoing final circuits apart from within the fettling/painting shops and wash rooms are to be retained & reused as they are currently installation. Presumed they are up to current regulations to be re-energised
| 4.07 | Allowed for new supplies to extract systems within both fettling / paint shops. Complete electrical install (LEV contractor will supply starters). New ventilations to be supplied & installed by others.
| 4.08 | Paint shop
| 4.08.1 | Electrical supply required – 3 Phase, 400V, 50Hz, 10amp with D Type Breaker
| 4.08.2 | Electrical wiring for ductwork package and fan installation.
| 4.09 | Fettling shop
| 4.09.1 | Grinding Filter -Electrical supply required – 3 Phase, 400V, 50Hz, 10amp with D Type Breaker
| 4.09.2 | Down Draft Bench - Electrical supply required – 1 Phase, 230V, 50Hz, 13amp (3 pin socket)
| 4.09.3 | Electrical control wiring (as necessary)
[5 empty] | Item 4 Total | 0
|  |  |  | To be carried forward to Collection |  | 0

## 5 Foundry Electrical Works
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow all preliminaries in connection with the works. This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
General notes
| 5 | FOUNDRY NEW WORKS TO FACILITATE LEV UPGRADES
| 5.01 | Utilising the spare capacity of the WALKWAY FOUNDRY DB install new 3 Phase, 400V, 50Hz, 10amp with D Type Breaker supply to extraction cabinet and downdraft benches at chalk press adjacent to the viewing gallery.
| 5.02 | Allowed for new supplies to extract systems within the Foundry. Complete electrical install (LEV contractor will supply starters). New ventilation to be supplied & installed by others.
| 5.03 | Include for electrical control wiring (as necessary)
| 5.04 | All existing outgoing final circuits apart from within the Foundry are to be retained & reused as they are currently installation. Presumed they are up to current regulations to be re-energised
[5 empty] | Item 5 Total | 0
|  |  |  | To be carried forward to Collection |  | 0

## 6 Provisional Sums
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow all preliminaries in connection with the works. This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
General notes
| 6 | PROVISIONAL COSTS
| 6.01 | Provisional Cost £5000.00 to be set against remedial works for Fettling/ Paint shops |  |  |  | 5000
| 6.02 | Provisional Cost £5000.00 to be set against remedial works for Foundry |  |  |  | 5000
[5 empty] | Item 2 Total | 10000
|  |  |  | To be carried forward to Collection |  | 10000

## 7 Collection
The Coffin Works, 13-15 Fleet Street, Jewellery Quarter, Birmingham B3 1JP Tel: 0121 773 5002
W: www.oliver-architecture.co.uk E: conservation@oliver-architecture.co.uk
FOUNDRY, BLISTS HILL VICTORIAN TOWN
LEV & ELECTRICAL UPGRADE PROJECT
April 2022 Version v.1 12/04/24
Outline Schedule of Works Allow This item deals with Electrical works to enable the LEV project across the Foundry and Fettling/Paint shops
| Item | Description | No | Unit | Rate | Total
General notes
| 7 | Collection
| 7.01 | ITEM 1 PRELIMINAIRES & GENERAL ITEMS
| 7.02 | ITEM 2 ENABLING WORKS
| 7.03 | ITEM 3 REMEDIAL WORKS
| 7.04 | ITEM 4 FETTLING-PAINT SHOP WORKS
| 7.05 | ITEM 5 FOUNDRY ELECTRICAL WORKS
| 7.06 | ITEM 6 PROVISIONAL SUMS |  |  |  | 10000
[5 empty] | Sub Total | 10000
| 8 | Contingency sum
| 8.01 | Contingency sum of 10% | 1 | Item |  | 1000
[5 empty] | Total excl contingency | 10000
[5 empty] | Total including contingency | 11000
plus VAT